## Slide 1
Compressor Specification
Flow Required (1465W heat removal)
m = 0.009 kg/s
Material: Silicone Elastomer
E = 20 MPa, ν = 0.5
Membrane Dimensions:
t = 1.1 cm, R = 6 cm
Displacement:
V = 330 cm3 , f = 1 Hz
Solar-Powered Phase Change Compressor
Addison Bender Jesse Diaz Emmanuel Ferdinand
Sponsor: Grant Peacock Advisors: Dr. Juan Ordoñez, John Dascomb
Project Need
Design a refrigerant compressor that can be driven by solar-generated steam.
 | Theoretical | Actual
Compression Power | 145 W | 70 W
Insolation Required | 6,891 W | 14,260 W
Thermal Energy Input Needed | 970 W | 2,007 W
Overall Efficiency | 2.10% | 1.02%
$/Watt | 9.63 | 19.93
Concept
Vent is closed. Pressure from boiler raises the membrane and compresses refrigerant.
Vent is opened. Steam is released and refrigerant is drawn into the upper chamber as the pressure in the lower chamber drops.
Vent is closed, cycle repeats.
s
T
T1 = 4°C
P1 = 338 kPa
1
2
3
4
T2 = 32.9°C
P2 = 771 kPa
T4 = 4°C
P4 = 338 kPa
R134a Ideal Vapor-Compression Refrigeration Cycle
T3 = 30°C
P3 = 771 kPa
δ
D
t
Chart: Initial Charge: 551 kPa
Chart: Initial Charge: 551kPa
Energy Analysis
Results
High pressure refrigerant to condenser
Low pressure refrigerant from evaporator.
Steam supply from boiler (175oC < T < 225oC)
Steam vent to atmosphere
High-use check valves constrain flow to one direction through the refrigerant loop as membrane oscillates.
Pressure relief valve prevents membrane blow-out if pressure builds up in steam chamber.
Fast-response solenoid valve controls steam pressure in the lower compressor chamber. (open: 0.5 s, closed: 0.5s)
Solenoid Control Circuit
Steam shut-off valve
High temperature silicon elastomer membrane
(rated for 316oC)
Conclusions
Membrane failed when steam was used. Successful test used compressed air.
Compression of refrigerant was achieved, though less than target.
Energy is lost when membrane is deformed and steam is vented.
High-use components diminish system reliability.